## Change History
Revision | Date | Description
1 | 2022-06-01 | Initial Release

## Buildings
Building Number | Building Name | BMS Name | BMS Vendor
4001 | Administration (previously Student Services) | SS | Siemens
4002 | Arts | ART | Siemens
4028 | Arts & Science | AS | Siemens
4030 | Engineering Management & Education | EME | Siemens
4020 | Fipke | FIP | Siemens
4000 | Library | LIB | Siemens
4006 | Central Heating Plant | CHP | Siemens
4021 | Geo Exchange | GEO | Siemens
4035 | Commons (previously TLC - Teaching & Learning Centre) | COM | Siemens
| Campus Wide | CAM | All
4008 | Mountain Weather Office | MWO | Kimco (Delta)
4003 | Science | SCI | Siemens
4004 | Creative and Critical Studies | CCS | Kimco (Delta)
4022 | University Centre | UNC | Kimco (Delta)
4005 | Gym | GYM | Siemens
4034 | Innovation Presinct Lab (also IP1 - Innovation Presinct 1) | IPL | Siemens
4099-23 | Office Modular 1 | OM1 | Siemens (integration only)
4042 | Plant Growth Facility | PGF | Kimco (Delta)
4023 | Nicola Residence | NIC | Kimco (Delta)
4040 | Skeena Residence | SKE | Siemens
4041 | Nechako Residence | NEC | Siemens
4033 | Reichwald Heath Sciences Centre | RHS | Johnson Controls
4032 | Daycare | DAY | Siemens (metering only)
4099-24 | Portable V | PBV | None
4013-4019 | Lower Cascades | LCAS | Siemens (metering only)
4098 | Quonset | QUO | Siemens (metering only)
4031 | Purcell Residence | PUR | Siemens
4010 | Monashee Residence | MON | Siemens (metering only)
4011 | Valhalla Residence | VAL | Siemens (metering only)
4009 | Similkameen Residence | SIM | Siemens (metering only)
4029 | Cassiar Residence | CAS | Siemens (metering only)
4039 | Engineering Design Lab Portable | EDL | Siemens

## Point Naming
TYPICAL POINT NAME: | O.{BldgName}.{SysName}.{EquipName}{EquipNumber}.{PointName}
DATE: | 2022-06-01
Revision: | 1
SYSTEM CODE | SYSTEM CODE DESCRIPTOR | EQUIPMENT CODE | EQUIPMENT CODE DESCRIPTOR | POINT CODE | POINT CODE DESCRIPTOR | VIRTUAL CODE | VIRTUAL CODE DESCRIPTOR
AH | AIR HANDLING UNIT & 2 DIGIT NUMBER | AFMS | AIR FLOW MONITORING STATION | GAS DETECTION |  | ALM | ALARM
CDW | CONDENSER WATER SYSTEM | BLR | BOILER & NUMBER | CO2 | CARBON DIOXIDE (INTEGRATION) | AMP | AMPERAGE (INTEGRATION)
CHW | CHILLED WATER SYSTEM | CH | CHILLER | EAC | EXHAUST AIR CO2 SENSOR | AUX | AUXILIARY
DCW | DOMESTIC COLD WATER | CT | COOLING TOWER | MAC | MIXED AIR CO2 SENSOR | BIAS | BIAS
DHW | DOMESTIC HOT WATER | CU | CONDENSING UNIT | NATGAS | NATURAL GAS | BSP.SP | BUIDLING STATIC STPT
EA | EXHAUST AIR | ECO | ECONOMIZER | NO2 | NITROGEN DIOXIDE | CMD | COMMAND
EXH | EXHAUST SYSTEM | EF | EXHAUST FAN UNIT | O2 | OXYGEN | COEF | COEFFICIENT
GLY | GLYCOL SYSTEM | GEN | GENERATOR | OAC | OUTSIDE AIR CO2 SENSOR | COMM | COMMUNICATION
ICE | ICE SYSTEM | FE## | FUME HOOD EXHAUST FAN | RAC | RETURN AIR CO2 SENSOR | CLG | COOLING
IND | INDUCTION SYSTEM | FM## | FLOW METER | RMC | ROOM CO2 SENSOR | CTL | CONTROL
KIT | KITCHEN SYSTEM | GH | GAS HEATER / GAS HEATING | SAC | SUPPLY AIR CO2 SENSOR | DSP.SP | DISCHARGE AIR STATIC STPT
MU | MAKEUP AIR UNIT & NUMBER (MATCH EQUIP TAG) | HE# | HEAT EXCHANGER & NUMBER | PM25 | PARTICULATE MATTER 2.5um | DAY | DAY
NPW | NON POTABLE WATER | HRC | HEAT RECLAIM COIL | PM10 | PARTICULATE MATTER 10um | DG | DERIVATIVE GAIN
PHT | PREHEAT HOT WATER | HRV## | HEAT RECOVERY VENTILATOR & NUMBER | TEMPERATURE |  | DWP.SP | DIFFERENTIAL PRESSURE SET-POINT
PHW | PRIMARY HOT WATER | HUM | HUMIDIFIER | EAT | EXHAUST AIR TEMPERATURE | EAF.SP | EXHAUST FLOW STPT
OA | OUTDOOR AIR | HW | HEAT WHEEL | HWR | HOT WATER RETURN | EASP.SP | EXHAUST AIR STATIC STPT
RA | RETURN AIR | P## | PUMP & NUMBER (INCLUDING BOOSTER PUMPS) | HWS | HOT WATER SUPPLY | ECO | ECONOMIZER MODE(FREE COOL)
MA | MIXED AIR | RF | RETURN FAN | LAT | LEAVING AIR TEMPERATURE | FLT | FAULT
RAD | RADIATION | SF | SUPPLY FAN | MAT | MIXED AIR TEMPERATURE | HTG | HEATING
SCHCW | SCHEDULED COLD WATER | SLAB | SLAB & NUMBER | OAT | OUTDOOR AIR TEMPERATURE | HL.SP | HIGH LIMIT STPT
SCHHW | SCHEDULED HOT WATER | RZ | Radiant Zone | PHT | PREHEAT AIR TEMPERATURE | IG | INTEGRAL GAIN
SCHW | SECONDARY CHILLED WATER | MAN | Manifold | RAT | RETURN AIR TEMPERATURE | ISO | ISOLATION
SHW | SECONDARY HOT WATER | SP | SUMP PUMP | DWT | DIFFERENTIAL WATER TEMP | kW | KILLOWATTS
SYS | SYSTEM | TK | TANK | RMT | ROOM TEMPERATURE | LA.ENTH | LEAVING AIR ENTHALPY
RTU | ROOF TOP UNIT | TF | TRANSFER FAN | RWT | RETURN WATER TEMPERATURE | LA.ENTH.SP | LEAVING AIR ENTHALPY STPT
LDES | LOW TEMPERATURE DISTRICT ENERGY | VFD | VARIABLE FREQUENCY DRIVE | SAT | SUPPLY AIR TEMPERATURE | LAG | LAG SYSTEM
MDES | MEDIUM TEMPERATURE DISTRICT ENERGY | VRF | VARIABLE REFRIGERANT FLOW | SWT | SUPPLY WATER TEMPERATURE | LEAD | LEAD SYSTEM
GEO | GEOTHERMAL EXCHANGE | STM | STEAM | BWT | BRIDGE WATER TEMPERATURE | LL.SP | LOW LIMIT SETPOINT
WS | WATER SYSTEM | AC | AIR COMPRESSOR | TMP | TEMPERATURE (OTHER THAN ABOVE) | MAT.SP | MIX AIR TEMPERATURE SETPOINT
HW | HEATING WATER | DX | DX COOLING STAGE ## |  |  | MAX | MAXIMUM
CW | COOLING WATER | HCP | HEATING COIL PUMP | PRESSURE |  | MIN | MINIMUM
FEX | Fume Hood Exaust | CCP | COOLING COIL PUMP | BSP | BUILDING STATIC PRESSURE | MODE | POINT MODE
SWR | Sewer | CMP | COMPRESSOR | HSP | HIGH STATIC DISCHARGE PRESSURE (SWITCH) | NGT | NIGHT
DE | District Energy | BEF | BENCH EXHAUST FAN | DSP | DISCHARGE AIR STATIC PRESSURE (ANALOG) | OA.ENTH | OUTSIDE AIR ENTHALPY
|  | GEF | GENERAL EXHAUST FAN | EAP | EXHAUST AIR PRESSURE (SWITCH) | OAF.SP | OUTSIDE FLOW STPT
|  | RPM | ROOM PRESSURE MONITOR & RM NUMBER | ESP | EXHAUST STATIC PRESSURE (ANALOG) | OCC | OCCUPANCY MODE
|  | SAV | SUPPLY AIR VALVE (Labs only, VAV otherwise) | EFIL | EXHAUST-FILTER PRESSURE | OF | OVERFLOW
|  | EAV | EXHAUST AIR VALVE | FFLT | FINAL-FILTER PRESSURE | OUT | OUTPUT
|  | RAV | RETURN AIR VALVE | MAP | MIXED AIR PRESSURE (SWITCH) | PDL | PEAK DEMAND LIMIT
|  | VAV | VARIABLE AIR VOLUME | MSP | MIX STATIC PRESSURE (ANALOG) | PG | PROPORTIONAL GAIN
|  | FHC | FUME HOOD CONTROLLER | PFIL | PRE-FILTER PRESSURE | LO | PID LOOP OUTPUT
|  | FC | FAN COIL | PRS | PRESSURE | PNU | PNEUMATIC
|  | CAV | Constant Air Volume Box | RAP | RETURN PRESSURE (SWITCH) | POS | POSITION
|  | TF | Transfer Fan | RSP | RETURN STATIC PRESSURE (ANALOG) | RA.ENTH | RETURM AIR ENTHALPY
|  | UH | Unit Heater | RGP | RETURN GLYCOL PRESSURE | RA.ENTH.SP | RTURN AIR ENTHALPY STPT
|  |  |  | RWP | RETURN WATER PRESSURE | RAF.SP | RETURN FLOW STPT
|  |  |  | SAP | SUPPLY AIR PRESSURE (SWITCH) | RAH.SP | RETURN AIR HUMIDITY STPT
|  |  |  | SSP | SUPPLY STATIC PRESSURE (ANALOG) | RASP.SP | RETURN AIR STATIC STPT
|  |  |  | SFIL | SUMMER FILTER PRESSURE | RAT.SP | RETURN AIR TEMPERATURE SETPOINT
|  |  |  | SGP | SUPPLY GLYCOL PRESSURE | SYS.RST | SYSTEM RESET
|  |  |  | SWP | SUPPLY WATER PRESSURE | RGT.SP | RETURN GLYCOL TEMPERATURE STPT
|  |  |  | VP | VELOCITY PRESSURE | RMH.SP | ROOM HUMIDITY SETPOINT
|  |  |  | DWP | DIFFERENTIAL WATER PRESSURE | RWT.SP | RETURN WATER TEMPERATURE STPT
|  |  |  | WFIL | WINTER FILTER PRESSURE | SA.ENTH | SUPPLY AIR ENTHALPY
|  |  |  | HFLT | HEPA FILTER | SA.ENTH.SP | SUPPLY AIR ENTHALPY STPT
|  |  |  | ACP | AIR COMPRESSOR PRESSURE | SAF.SP | SUPPLY FLOW STPT
|  |  |  | VALVES |  | SAH.SP | SUPPLY AIR HUMIDITY STPT
|  |  |  | BPV | BYPASS VALVE | SASP.SP | SUPPLY AIR STATIC STPT
|  |  |  | CBV | CHILLED BEAM VALVE | SAT.SP | SUPPLY AIR TEMPERATURE SETPOINT
|  |  |  | CCV | COOLING COIL VALVE | SP | SETPOINT
|  |  |  | HCV | HEATINIG COIL VAVLVE | SGT.SP | SUPPLY GLYCOL TEMPERATURE STPT
|  |  |  | HUMV | HUMIDITY STEAM VALVE | SO | SWITCH OVER
|  |  |  | PHCV | PREHEAT COIL VALVE | S | STATUS
|  |  |  | RADV | RADIATION COIL VALVE | SUMMER | SUMMER
|  |  |  | RHCV | REHEAT COIL VALVE | SWT.SP | SUPPLY WATER TEMPERATURE STPT
|  |  |  | VLV## | VALVE & NUMBER | V | VOLTAGE (INTEGRATION)
|  |  |  | CV | Coil Valve / Control Valve | VAC | VACANT
|  |  |  | ISO | Isolation Valve | WINTER | WINTER
|  |  |  | SWV | Supply Water Valve | WTR | WATER
|  |  |  | RWV | Return Water Valve | OSET | OFFSET
|  |  |  | DAMPERS |  | OVR | OVERRIDE
|  |  |  | BPD | BYPASS DAMPER | LTG | LIGHTING
|  |  |  | EAD | EXHAUST AIR DAMPER | PWR | POWER
|  |  |  | FACED | FACE DAMPER | PF | POWER FACTOR
|  |  |  | IAD | ISOLATION AIR DAMPER | CRT | CONSUMPTION RUNNING TOTAL
|  |  |  | MAD | MIXED AIR DAMPER | NH | NIGHT SET BACK HEATING
|  |  |  | OAD | OUTDOOR AIR DAMPER | SCH | SCHEDULE
|  |  |  | RAD | RETURN AIR DAMPER | ST | SECONDS TIMER
|  |  |  | SAD | SUPPLY AIR DAMPER | SEC | SECURITY
|  |  |  | HUMIDITY |  | CFH | CALL FOR HEAT
|  |  |  | EAH | EXHAUST AIR HUMIDITY | CFC | CALL FOR COOLING
|  |  |  | OAH | OUTDOOR AIR HUMIDITY | PRG | PURGE
|  |  |  | RAH | RETURN AIR HUMIDITY | AVG | AVERAGE
|  |  |  | RMH | ROOM HUMIDITY | DL | DEMAND LIMIT (CHILLER)
|  |  |  | SAH | SUPPLY AIR HUMIDITY | TMR | TIMER (OTHER THAN SECONDS)
|  |  |  | VELOCITY/FLOW MONITORING |  | CNT | PROGRAM COUNTER
|  |  |  | EAF | EXHAUST AIR FLOW | FLG | FLAG
|  |  |  | EAV | EXHAUST AIR VELOCITY | ADJ | ADJUST
|  |  |  | RAF | RETURN AIR FLOW | WUM | Warm-Up Mode
|  |  |  | RAV | RETURN AIR VELOCITY
|  |  |  | SAF | SUPPLY AIR FLOW
|  |  |  | SAV | SUPPLY AIR VELOCITY
METERING
|  |  |  | EMB | Energy Meter
|  |  |  | GM | Gas Meter
|  |  |  | GMB | Gas Meter
|  |  |  | BTU | BTU Meter
|  |  |  | SWF | Supply Water Flow
|  |  |  | RWF | Return Water Flow
|  |  |  | D | Demand
|  |  |  | CRT | Consumption Running Total
|  |  |  | AP | Apparent Power
|  |  |  | APP.PWR | Apparent Power
|  |  |  | PF | Power Factor
|  |  |  | FLOW | Flow
|  |  |  | KW | Energy in kW
|  |  |  | KWH | Consumption in kWh
|  |  |  | COOL.KW | COOLING ENERGY
|  |  |  | HEAT.KW | HEATING ENERGY
|  |  |  | DHW | Domestic Hot Water
|  |  |  | DCW | Domestic Cold Water
|  |  |  | DMW | Domestic Makeup Water
|  |  |  | PT | Pulse Totalizer
|  |  |  | VT | Volume Totalizer
|  |  |  | DEM | Digital Energy Meter
|  |  |  | CH | Chiller
|  |  |  | WSHP | Water Source Heat Pump
|  |  |  | ASHP | Air Source Heat Pump
|  |  |  | IWM | Irrigation Water Meter
MISCELLANEOUS
|  |  |  | ALM | ALARM
|  |  |  | ENB | ENABLE
|  |  |  | ENTH | ENTHALPY
|  |  |  | FLT | FAULT / FILTER
|  |  |  | FBK | FEEDBACK
|  |  |  | HL | HIGH LEVEL OR LIMIT
|  |  |  | LL | LOW LEVEL OR LIMIT
|  |  |  | LO | LOW
|  |  |  | LTD | LOW TEMP DETECTOR
|  |  |  | REF## | REFRIGERANT SENSOR & NUMBER
|  |  |  | RSD | RETURN SMOKE DETECTION
|  |  |  | SP | SET-POINT RESET
|  |  |  | SPD | SPEED SIGNAL (PERCENT)
|  |  |  | SSD | SUPPLY SMOKE DETECTION
|  |  |  | TBL | TROUBLE
|  |  |  | VIB | VIBRATION
|  |  |  | ES | END SWITCH
|  |  |  | MT | MOTION
|  |  |  | FS | FLOW SWITCH
|  |  |  | DC | DUST COLLECTOR
|  |  |  | DS | DOOR SWITCH (Overhead or Door)

## Device Naming
Device Naming Convention By Vendor |  | Equipment Identifiers | Description
Siemens: | UBCONODEXX | LRC | LAB RM CONTROLLER & LAB NUMBER
| XX - Field Panel Number must be unique | PRC | PRESSURIZED ROOM CONTROLLER & RM NUMBER
Kimco/Delta: | Use BACnet Instance Number as primary identifier | RPM | ROOM PRESSURE MONITOR & RM NUMBER
Johnson Controls: | AAA-BBB-XX | SAV | SUPPLY AIR VALVE (Labs only, VAV otherwise)
| AAA - Building Identifier (see buildings tab)) | EAV | EXHAUST AIR VALVE
| BBB - Controller Type (ex. NAE or NCE) | RAV | RETURN AIR VALVE
| XX - Controller number must be unique | VAV | VARIABLE AIR VOLUME
|  | FHC | FUME HOOD CONTROLLER
Terminal Units Naming: |  | FC | FAN COIL
All equipment to be named with prefix "O." for Okanagan Campus |  | CAV | Constant Air Volume Box
O.AAA.BBB.XX |  | TF | Transfer Fan
| AAA - Building Identifier (see buildings tab)) | UH | Unit Heater
| BBB - Equipment Identifier (See chart to right) | FPB | Fan Powered Box
| XX - Equipment Number 01 through 99, use 3 digitis if more than 99 devices exist in a building | AC | Air Conditioning Unit (cooling compressor only)
|  | HP | Heat Pump
VFD Naming |  | RHC | Reheat Coil
Similar to terminal unit naming, with "VFD" suffix. |  | RHE | Reheat Coil Electric
O.AAA.BBB.CCC.VFD |  | RAD | Radiant panel / wall fin
AAA - Building Identifier (see buildings tab))
BBB - Equipment Identifier (See chart to right)
CCC - VFD Identifier (see chart to right)
XX - Equipment Number 01 through 99, use 3 digitis if more than 99 devices exist in a building
|  | VFD Identifiers | Description
|  | AH | Air Handler
|  | MU | Makeup Air
|  | HW | Heating Water
|  | CW | Cooling Water
|  | SF | Supply Fan
|  | RF | Return Fan
|  | EF | Exhaust Fan
|  | P | Pump